矽膠石附件

Improving Silica Gel Reactivation

Silica gel desiccant reactivation is a common operating procedure regularly used and

performed to remove moisture from saturated material.

Silica gel is used throughout industry to adsorb moisture and maintain low relative humidity

thereby preventing product contamination and degradation. Silica gel is capable of adsorbing

up to thirty percent of its own weight of water vapour.

The majority of Transformer Breathers used by the power generation industry contain

indicating silica gel. Silica gel is available in two primary types indicating and non-indicating.

The indicating property is achieved by impregnation with cobalt chloride salt which is

sensitive to water vapour.

See caution note as cobalt chloride impregnated silica gel is now carcinogenic.

Ineffective reactivation control can result in Transformer Breathers being maintained by up to

three times more than is necessary.

Shorter maintenance periods have an impact on both time and cost.

The use of valved Transformer Breathers has eliminated the need to maintain the oil seal

fluid level and combining this with improved reactivation contributes to further savings by

extending the average maintenance period.

This article suggests a number of simple improvements to improve the practice and

procedures for reactivation of silica gel.

| The Brownell 1005 reactivator being filled with cobalt chloride impregnated silica gel. |  |  |
| --- | --- | --- |
|  | Graph indicating the rate of moisture loss during reactivation from the Brownell 1005 desiccant reactivator. |  |

Indicating Silica Gel

Indicating silica gel is used throughout the power generation and transmission industry for

Transformer Breathers to protect the heat transfer cooling oil from moisture (condensed

water) contamination. One of the principal reasons for the use of indicating silica gel is its

ability to release adsorbed moisture when heated to a temperature of over 100oC. This

means it can recovered and used again. Indicating silica gel can theoretically be reactivated

a number of times. This will depend on several key factors including the environmental

conditions during use the reactivation temperature and reactivation procedure.

The Brownell 1005 reactivator being filled with Envirogel.

Although this may seem a simple procedure inadequate control and poor process techniques

can have a major impact on maintenance schedules by reducing the average time between

reactivation and replacement of exhausted indicating silica gel. Indicating silica gel is a

silica-based material capable of adsorbing 25% of its own weight in moisture. The most

widely used indicating silica gel was impregnated with cobalt chloride that gives the silica gel

its activity saturation indicator changing from a blue colour to pink when a 10-12% moisture

loading (by weight) of the desiccant is exceeded.

Warning

Cobalt chloride impregnated silica gel has now been classified as carcinogenic.

Beaded indicating silica gel is the best material to use in transformer breathers as it provides

high resistance to attrition (dusting breakdown) during handling and regular bed packing

providing uniform flow rate characteristics. The saturation indicator changes from a blue

colour to pink when the silica gel requires reactivation or replacement. The saturation

indicator can be directly related to the equilibrium relative humidity of the fluid (oil).

Maintaining the moisture level of oil to a maximum of content of 15 PPM is a typical

requirement.

The Brownell alternative to cobalt impregnated silica gel is ENVIROGEL ENVIROGEL can

be safely reactivated.

Warning

It is an essential safety requirement that the outlet exhaust vent from the reactivation

equipment is piped to the outside of the building/room into an adequate ventilated space.

If you require any specific advice for reactivation of desiccants please call our help lines or

e-mail for assistance to partridgem@brownell.co.uk

The Problems

One or a combination of the following factors can affect effective reactivation;

1. Failure to achieve an equal temperature of more than 100 C throughout the entire

Silica gel desiccant.

2.An inadequate supply of hot air to carry away the moisture driven off during

reactivation.

3.Considering the reactivation process is complete when the activity indicator of the

Silica gel displays an active colour.

4.Overheating during reactivation which can cause damage to the desiccant

5.structurereducing the moisture adsorption capacity.

6.Use of the wrong type of equipment for reactivation.

7.Attempting to reactivate silica gel, which has been contaminated with oil.

8.Not storing reactivated silica gel in a sealed airtight container.

Industrial Examples

There are a number of examples of poor reactivation processing currently used in industry.

Many poor reactivation procedures derive from a less than clear understanding of simple

procedures and controls required which will considerably improve the reactivation process.

Many users consider placing silica gel in a warm oven as an adequate method to remove

headsorbed water.

The use of gas ovens should be avoided and microwave cookers are likely to damage the

structure of the silica gel.

The Effects

Silica gel which has been subjected to temperatures in excess of 150oC is likely to be

discoloured to a brown or blackened state. If the silica gel has been subjected to overheating

the adsorption capacity will have been adversely effected. If silica gel that has been

contaminated with oil is reactivated the adsorption capacity will be effected and the oil

contamination could be readily transferred to silica gel contained in the reactivation unit.

Silica gel, which has a brown colour and emits odour during storage or reactivation, is often

an indication of contamination. The reactivation of contaminated desiccant causes the oil to

solidify within the structure of the desiccant resulting in a 50% reduction in adsorption

capacity.Health and safety consideration must always be given to the reactivation of silica

gel. It is an essential safety requirement that the outlet port of the reactivation equipment is

vented to an atmosphere which is external of the workshop or facility where the process is

being carried out.The use of an adsorption filter may also be necessary if there is a risk that

unidentifiable contaminates may be expelled during reactivation.

Silica Gel Activity Saturation Indicator.

One of the most important factors from the above to understand is the meaning and purpose

Of the activity indicator. When new or replacement desiccant is supplied by the manufacturer

the desiccant will have a maximum moisture loading of 2% by weight.

The desiccant will therefore adsorb 10% moisture loading which will cause the activity

indicator to change from a blue to pink colour. At this time the desiccant must be recharged

or replaced. The activity indicator changes colour on a narrow band of approximately 2%

moisture content and this is the primary cause of poor desiccant reactivation.

When the desiccant is heated the activity indicator will change from its saturated colour to its

active colour early in the reactivation process as a consequence of the narrow change band.

If the desiccant is considered to be reactivated at this time the residual moisture loading

could be as high as 10%. The desiccant has therefore not been reactivated to remove the

adsorbed moisture to the 2% level as supplied by the manufacturer.

When the desiccant that has been poorly reactivated is used the activity indicator will change

rapidly from the active colour to saturated indication depending on the duty cycle and the

weather.

The desiccant will require reactivation and so the cycle begins again at much shorter

Intervals than the original desiccant charge.Any of the above factors for poor desiccant

reactivation will have a similar result of the activity indicator changing rapidly following

reactivation. Improving the reactivation process is simple and often only requires a

modification to existing procedures.

The Solution

When reactivating desiccant it is vital that the activity indicator is not used to control the

process as previously discussed.

- As a general rule saturated desiccant will require a minimum of 4-6 hours at a

temperature of between 105-130oC throughout the entire desiccant bed for the

reactivation process to be effective and reduce the adsorbed moisture to less than 2% by

weight.

Caution

Some desiccants are seriously damaged and can release toxic chemicals if overheated.

- Reactivation should be carried out in a ventilated electric oven. A sealed oven will

limit  the moisture liberated and prevent efficient reactivation. Gas ovens and

microwave cookers are also not suitable for reactivation.

- Devices that pass warm air through the desiccant bed changing the activity indicator

to blue should be avoided.

- Ideally after reactivation the desiccant must be placed in a sealed container and

allowed to cool. The reactivated desiccant should not be stored in a warm oven at

60oC as this will cause partial saturation of the desiccant although the activity

indicator may remain stable.

- There are a number of proprietary reactivation equipment’s available on the market.

Typical equipment should be able to reactivate 25 kilograms of saturated silica gel

using a standard 13amp domestic supply.

- To validate reactivation efficiency a fundamental weight loss test conducted before

and after processing will provide the amount of moisture loss data.

- A supply of pre-heated air is an integral requirement for an efficient reactivation

process. For saturated desiccant a minimum air flow of between 5-10 cubic feet per

minute.

Conclusion

The process of reactivation requires the application and achievement of a number

of  simple controls for optimum efficiency. By following and adopting the above

reactivation practice and procedures we are confident  you will record improvements

for the maintenance time and performance of the silica gel.